## calcs
Enter SEL-487B Relay settings |  |  |  | O87P and SLP2 intersection
O87P = | 1 | pu |  | IRT = | 1.25 | pu
TAP01 = | 5 | amps
TAP02 = | 5 | amps |  | Choose IRT for internal fault |  |  |  | IOP on the slope
SLP2 = | 80 | % |  | IRT = | 2 | pu |  | IOP = | 1.6 | pu
Initial current (10 cycles) |  |  |  | Pre-Fault results |  |  | Legend
(puts relay in high security mode) |  |  |  | IOP = | 0 | pu | Enter SEL-487B Relay settings
I01 = | 9 | amps < | 0° | IRT = | 3.6 | pu | Enter restraint current for internal fault
I02 = | 9 | amps < | 180° | slope = | 0 | % | Vary input 2 test current for internal fault
Slope 2 test currents (10 cycles) |  |  |  | Fault results
I01 = | 9 | amps < | 0° | IOP = | 1.62 | pu
a I02 = | 0.9 | amps < | 180° | IRT = | 1.98 | pu
a ¦I02¦ @ balance point = |  | 1 | amps | slope = | 81.8182 | %
Outcome
b Trip = | YES! |  |  | b Monitor Relay Word Bit (RWB) 87R1

## plot
|  | test point |  | pre-fault
IRT | diff characteristic | IRT | IOP | IRT | IOP
0 | 1 | 1.98 | 1.62 | 3.6 | 0
0.01 | 1
0.02 | 1
0.03 | 1
0.04 | 1
0.05 | 1
0.06 | 1
0.07 | 1
0.08 | 1
0.09 | 1
0.1 | 1
0.11 | 1
0.12 | 1
0.13 | 1
0.14 | 1
0.15 | 1
0.16 | 1
0.17 | 1
0.18 | 1
0.19 | 1
0.2 | 1
0.21 | 1
0.22 | 1
0.23 | 1
0.24 | 1
0.25 | 1
0.26 | 1
0.27 | 1
0.28 | 1
0.29 | 1
0.3 | 1
0.31 | 1
0.32 | 1
0.33 | 1
0.34 | 1
0.35 | 1
0.36 | 1
0.37 | 1
0.38 | 1
0.39 | 1
0.4 | 1
0.41 | 1
0.42 | 1
0.43 | 1
0.44 | 1
0.45 | 1
0.46 | 1
0.47 | 1
0.48 | 1
0.49 | 1
0.5 | 1
0.51 | 1
0.52 | 1
0.53 | 1
0.54 | 1
0.55 | 1
0.56 | 1
0.57 | 1
0.58 | 1
0.59 | 1
0.6 | 1
0.61 | 1
0.62 | 1
0.63 | 1
0.64 | 1
0.65 | 1
0.66 | 1
0.67 | 1
0.68 | 1
0.69 | 1
0.7 | 1
0.71 | 1
0.72 | 1
0.73 | 1
0.74 | 1
0.75 | 1
0.76 | 1
0.77 | 1
0.78 | 1
0.79 | 1
0.8 | 1
0.81 | 1
0.82 | 1
0.83 | 1
0.84 | 1
0.85 | 1
0.86 | 1
0.87 | 1
0.88 | 1
0.89 | 1
0.9 | 1
0.91 | 1
0.92 | 1
0.93 | 1
0.94 | 1
0.95 | 1
0.96 | 1
0.97 | 1
0.98 | 1
0.99 | 1
1 | 1
1.01 | 1
1.02 | 1
1.03 | 1
1.04 | 1
1.05 | 1
1.06 | 1
1.07 | 1
1.08 | 1
1.09 | 1
1.1 | 1
1.11 | 1
1.12 | 1
1.13 | 1
1.14 | 1
1.15 | 1
1.16 | 1
1.17 | 1
1.18 | 1
1.19 | 1
1.2 | 1
1.21 | 1
1.22 | 1
1.23 | 1
1.24 | 1
1.25 | 1
1.26 | 1.008
1.27 | 1.016
1.28 | 1.024
1.29 | 1.032
1.3 | 1.04
1.31 | 1.048
1.32 | 1.056
1.33 | 1.064
1.34 | 1.072
1.35 | 1.08
1.36 | 1.088
1.37 | 1.096
1.38 | 1.104
1.39 | 1.112
1.4 | 1.12
1.41 | 1.128
1.42 | 1.136
1.43 | 1.144
1.44 | 1.152
1.45 | 1.16
1.46 | 1.168
1.47 | 1.176
1.48 | 1.184
1.49 | 1.192
1.5 | 1.2
1.51 | 1.208
1.52 | 1.216
1.53 | 1.224
1.54 | 1.232
1.55 | 1.24
1.56 | 1.248
1.57 | 1.256
1.58 | 1.264
1.59 | 1.272
1.6 | 1.28
1.61 | 1.288
1.62 | 1.296
1.63 | 1.304
1.64 | 1.312
1.65 | 1.32
1.66 | 1.328
1.67 | 1.336
1.68 | 1.344
1.69 | 1.352
1.7 | 1.36
1.71 | 1.368
1.72 | 1.376
1.73 | 1.384
1.74 | 1.392
1.75 | 1.4
1.76 | 1.408
1.77 | 1.416
1.78 | 1.424
1.79 | 1.432
1.8 | 1.44
1.81 | 1.448
1.82 | 1.456
1.83 | 1.464
1.84 | 1.472
1.85 | 1.48
1.86 | 1.488
1.87 | 1.496
1.88 | 1.504
1.89 | 1.512
1.9 | 1.52
1.91 | 1.528
1.92 | 1.536
1.93 | 1.544
1.94 | 1.552
1.95 | 1.56
1.96 | 1.568
1.97 | 1.576
1.98 | 1.584
1.99 | 1.592
2 | 1.6
2.01 | 1.608
2.02 | 1.616
2.03 | 1.624
2.04 | 1.632
2.05 | 1.64
2.06 | 1.648
2.07 | 1.656
2.08 | 1.664
2.09 | 1.672
2.1 | 1.68
2.11 | 1.688
2.12 | 1.696
2.13 | 1.704
2.14 | 1.712
2.15 | 1.72
2.16 | 1.728
2.17 | 1.736
2.18 | 1.744
2.19 | 1.752
2.2 | 1.76
2.21 | 1.768
2.22 | 1.776
2.23 | 1.784
2.24 | 1.792
2.25 | 1.8
2.26 | 1.808
2.27 | 1.816
2.28 | 1.824
2.29 | 1.832
2.3 | 1.84
2.31 | 1.848
2.32 | 1.856
2.33 | 1.864
2.34 | 1.872
2.35 | 1.88
2.36 | 1.888
2.37 | 1.896
2.38 | 1.904
2.39 | 1.912
2.4 | 1.92
2.41 | 1.928
2.42 | 1.936
2.43 | 1.944
2.44 | 1.952
2.45 | 1.96
2.46 | 1.968
2.47 | 1.976
2.48 | 1.984
2.49 | 1.992
2.5 | 2
2.51 | 2.008
2.52 | 2.016
2.53 | 2.024
2.54 | 2.032
2.55 | 2.04
2.56 | 2.048
2.57 | 2.056
2.58 | 2.064
2.59 | 2.072
2.6 | 2.08
2.61 | 2.088
2.62 | 2.096
2.63 | 2.104
2.64 | 2.112
2.65 | 2.12
2.66 | 2.128
2.67 | 2.136
2.68 | 2.144
2.69 | 2.152
2.7 | 2.16
2.71 | 2.168
2.72 | 2.176
2.73 | 2.184
2.74 | 2.192
2.75 | 2.2
2.76 | 2.208
2.77 | 2.216
2.78 | 2.224
2.79 | 2.232
2.8 | 2.24
2.81 | 2.248
2.82 | 2.256
2.83 | 2.264
2.84 | 2.272
2.85 | 2.28
2.86 | 2.288
2.87 | 2.296
2.88 | 2.304
2.89 | 2.312
2.9 | 2.32
2.91 | 2.328
2.92 | 2.336
2.93 | 2.344
2.94 | 2.352
2.95 | 2.36
2.96 | 2.368
2.97 | 2.376
2.98 | 2.384
2.99 | 2.392
3 | 2.4
3.01 | 2.408
3.02 | 2.416
3.03 | 2.424
3.04 | 2.432
3.05 | 2.44
3.06 | 2.448
3.07 | 2.456
3.08 | 2.464
3.09 | 2.472
3.1 | 2.48
3.11 | 2.488
3.12 | 2.496
3.13 | 2.504
3.14 | 2.512
3.15 | 2.52
3.16 | 2.528
3.17 | 2.536
3.18 | 2.544
3.19 | 2.552
3.2 | 2.56
3.21 | 2.568
3.22 | 2.576
3.23 | 2.584
3.24 | 2.592
3.25 | 2.6
3.26 | 2.608
3.27 | 2.616
3.28 | 2.624
3.29 | 2.632
3.3 | 2.64
3.31 | 2.648
3.32 | 2.656
3.33 | 2.664
3.34 | 2.672
3.35 | 2.68
3.36 | 2.688
3.37 | 2.696
3.38 | 2.704
3.39 | 2.712
3.4 | 2.72
3.41 | 2.728
3.42 | 2.736
3.43 | 2.744
3.44 | 2.752
3.45 | 2.76
3.46 | 2.768
3.47 | 2.776
3.48 | 2.784
3.49 | 2.792
3.5 | 2.8
3.51 | 2.808
3.52 | 2.816
3.53 | 2.824
3.54 | 2.832
3.55 | 2.84
3.56 | 2.848
3.57 | 2.856
3.58 | 2.864
3.59 | 2.872
3.6 | 2.88
3.61 | 2.888
3.62 | 2.896
3.63 | 2.904
3.64 | 2.912
3.65 | 2.92
3.66 | 2.928
3.67 | 2.936
3.68 | 2.944
3.69 | 2.952
3.7 | 2.96
3.71 | 2.968
3.72 | 2.976
3.73 | 2.984
3.74 | 2.992
3.75 | 3
3.76 | 3.008
3.77 | 3.016
3.78 | 3.024
3.79 | 3.032
3.8 | 3.04
3.81 | 3.048
3.82 | 3.056
3.83 | 3.064
3.84 | 3.072
3.85 | 3.08
3.86 | 3.088
3.87 | 3.096
3.88 | 3.104
3.89 | 3.112
3.9 | 3.12
3.91 | 3.128
3.92 | 3.136
3.93 | 3.144
3.94 | 3.152
3.95 | 3.16
3.96 | 3.168
3.97 | 3.176
3.98 | 3.184
3.99 | 3.192
4 | 3.2
4.01 | 3.208
4.02 | 3.216
4.03 | 3.224
4.04 | 3.232
4.05 | 3.24
4.06 | 3.248
4.07 | 3.256
4.08 | 3.264
4.09 | 3.272
4.1 | 3.28
4.11 | 3.288
4.12 | 3.296
4.13 | 3.304
4.14 | 3.312
4.15 | 3.32
4.16 | 3.328
4.17 | 3.336
4.18 | 3.344
4.19 | 3.352
4.2 | 3.36
4.21 | 3.368
4.22 | 3.376
4.23 | 3.384
4.24 | 3.392
4.25 | 3.4
4.26 | 3.408
4.27 | 3.416
4.28 | 3.424
4.29 | 3.432
4.3 | 3.44
4.31 | 3.448
4.32 | 3.456
4.33 | 3.464
4.34 | 3.472
4.35 | 3.48
4.36 | 3.488
4.37 | 3.496
4.38 | 3.504
4.39 | 3.512
4.4 | 3.52
4.41 | 3.528
4.42 | 3.536
4.43 | 3.544
4.44 | 3.552
4.45 | 3.56
4.46 | 3.568
4.47 | 3.576
4.48 | 3.584
4.49 | 3.592
4.5 | 3.6
4.51 | 3.608
4.52 | 3.616
4.53 | 3.624
4.54 | 3.632
4.55 | 3.64
4.56 | 3.648
4.57 | 3.656
4.58 | 3.664
4.59 | 3.672
4.6 | 3.68
4.61 | 3.688
4.62 | 3.696
4.63 | 3.704
4.64 | 3.712
4.65 | 3.72
4.66 | 3.728
4.67 | 3.736
4.68 | 3.744
4.69 | 3.752
4.7 | 3.76
4.71 | 3.768
4.72 | 3.776
4.73 | 3.784
4.74 | 3.792
4.75 | 3.8
4.76 | 3.808
4.77 | 3.816
4.78 | 3.824
4.79 | 3.832
4.8 | 3.84
4.81 | 3.848
4.82 | 3.856
4.83 | 3.864
4.84 | 3.872
4.85 | 3.88
4.86 | 3.888
4.87 | 3.896
4.88 | 3.904
4.89 | 3.912
4.9 | 3.92
4.91 | 3.928
4.92 | 3.936
4.93 | 3.944
4.94 | 3.952
4.95 | 3.96
4.96 | 3.968
4.97 | 3.976
4.98 | 3.984
4.99 | 3.992
5 | 4
5.01 | 4.008
5.02 | 4.016
5.03 | 4.024
5.04 | 4.032
5.05 | 4.04
5.06 | 4.048
5.07 | 4.056
5.08 | 4.064
5.09 | 4.072
5.1 | 4.08
5.11 | 4.088
5.12 | 4.096
5.13 | 4.104
5.14 | 4.112
5.15 | 4.12
5.16 | 4.128
5.17 | 4.136
5.18 | 4.144
5.19 | 4.152
5.2 | 4.16
5.21 | 4.168
5.22 | 4.176
5.23 | 4.184
5.24 | 4.192
5.25 | 4.2
5.26 | 4.208
5.27 | 4.216
5.28 | 4.224
5.29 | 4.232
5.3 | 4.24
5.31 | 4.248
5.32 | 4.256
5.33 | 4.264
5.34 | 4.272
5.35 | 4.28
5.36 | 4.288
5.37 | 4.296
5.38 | 4.304
5.39 | 4.312
5.4 | 4.32
5.41 | 4.328
5.42 | 4.336
5.43 | 4.344
5.44 | 4.352
5.45 | 4.36
5.46 | 4.368
5.47 | 4.376
5.48 | 4.384
5.49 | 4.392
5.5 | 4.4
5.51 | 4.408
5.52 | 4.416
5.53 | 4.424
5.54 | 4.432
5.55 | 4.44
5.56 | 4.448
5.57 | 4.456
5.58 | 4.464
5.59 | 4.472
5.6 | 4.48
5.61 | 4.488
5.62 | 4.496
5.63 | 4.504
5.64 | 4.512
5.65 | 4.52
5.66 | 4.528
5.67 | 4.536
5.68 | 4.544
5.69 | 4.552
5.7 | 4.56
5.71 | 4.568
5.72 | 4.576
5.73 | 4.584
5.74 | 4.592
5.75 | 4.6
5.76 | 4.608
5.77 | 4.616
5.78 | 4.624
5.79 | 4.632
5.8 | 4.64
5.81 | 4.648
5.82 | 4.656
5.83 | 4.664
5.84 | 4.672
5.85 | 4.68
5.86 | 4.688
5.87 | 4.696
5.88 | 4.704
5.89 | 4.712
5.9 | 4.72
5.91 | 4.728
5.92 | 4.736
5.93 | 4.744
5.94 | 4.752
5.95 | 4.76
5.96 | 4.768
5.97 | 4.776
5.98 | 4.784
5.99 | 4.792
6 | 4.8
6.01 | 4.808
6.02 | 4.816
6.03 | 4.824
6.04 | 4.832
6.05 | 4.84
6.06 | 4.848
6.07 | 4.856
6.08 | 4.864
6.09 | 4.872
6.1 | 4.88
6.11 | 4.888
6.12 | 4.896
6.13 | 4.904
6.14 | 4.912
6.15 | 4.92
6.16 | 4.928
6.17 | 4.936
6.18 | 4.944
6.19 | 4.952
6.2 | 4.96
6.21 | 4.968
6.22 | 4.976
6.23 | 4.984
6.24 | 4.992
6.25 | 5
6.26 | 5.008
6.27 | 5.016
6.28 | 5.024
6.29 | 5.032
6.3 | 5.04
6.31 | 5.048
6.32 | 5.056
6.33 | 5.064
6.34 | 5.072
6.35 | 5.08
6.36 | 5.088
6.37 | 5.096
6.38 | 5.104
6.39 | 5.112
6.4 | 5.12
6.41 | 5.128
6.42 | 5.136
6.43 | 5.144
6.44 | 5.152
6.45 | 5.16
6.46 | 5.168
6.47 | 5.176
6.48 | 5.184
6.49 | 5.192
6.5 | 5.2
6.51 | 5.208
6.52 | 5.216
6.53 | 5.224
6.54 | 5.232
6.55 | 5.24
6.56 | 5.248
6.57 | 5.256
6.58 | 5.264
6.59 | 5.272
6.6 | 5.28
6.61 | 5.288
6.62 | 5.296
6.63 | 5.304
6.64 | 5.312
6.65 | 5.32
6.66 | 5.328
6.67 | 5.336
6.68 | 5.344
6.69 | 5.352
6.7 | 5.36
6.71 | 5.368
6.72 | 5.376
6.73 | 5.384
6.74 | 5.392
6.75 | 5.4
6.76 | 5.408
6.77 | 5.416
6.78 | 5.424
6.79 | 5.432
6.8 | 5.44
6.81 | 5.448
6.82 | 5.456
6.83 | 5.464
6.84 | 5.472
6.85 | 5.48
6.86 | 5.488
6.87 | 5.496
6.88 | 5.504
6.89 | 5.512
6.9 | 5.52
6.91 | 5.528
6.92 | 5.536
6.93 | 5.544
6.94 | 5.552
6.95 | 5.56
6.96 | 5.568
6.97 | 5.576
6.98 | 5.584
6.99 | 5.592
7 | 5.6
7.01 | 5.608
7.02 | 5.616
7.03 | 5.624
7.04 | 5.632
7.05 | 5.64
7.06 | 5.648
7.07 | 5.656
7.08 | 5.664
7.09 | 5.672
7.1 | 5.68
7.11 | 5.688
7.12 | 5.696
7.13 | 5.704
7.14 | 5.712
7.15 | 5.72
7.16 | 5.728
7.17 | 5.736
7.18 | 5.744
7.19 | 5.752
7.2 | 5.76
7.21 | 5.768
7.22 | 5.776
7.23 | 5.784
7.24 | 5.792
7.25 | 5.8
7.26 | 5.808
7.27 | 5.816
7.28 | 5.824
7.29 | 5.832
7.3 | 5.84
7.31 | 5.848
7.32 | 5.856
7.33 | 5.864
7.34 | 5.872
7.35 | 5.88
7.36 | 5.888
7.37 | 5.896
7.38 | 5.904
7.39 | 5.912
7.4 | 5.92
7.41 | 5.928
7.42 | 5.936
7.43 | 5.944
7.44 | 5.952
7.45 | 5.96
7.46 | 5.968
7.47 | 5.976
7.48 | 5.984
7.49 | 5.992
7.5 | 6
7.51 | 6.008
7.52 | 6.016
7.53 | 6.024
7.54 | 6.032
7.55 | 6.04
7.56 | 6.048
7.57 | 6.056
7.58 | 6.064
7.59 | 6.072
7.6 | 6.08
7.61 | 6.088
7.62 | 6.096
7.63 | 6.104
7.64 | 6.112
7.65 | 6.12
7.66 | 6.128
7.67 | 6.136
7.68 | 6.144
7.69 | 6.152
7.7 | 6.16
7.71 | 6.168
7.72 | 6.176
7.73 | 6.184
7.74 | 6.192
7.75 | 6.2
7.76 | 6.208
7.77 | 6.216
7.78 | 6.224
7.79 | 6.232
7.8 | 6.24
7.81 | 6.248
7.82 | 6.256
7.83 | 6.264
7.84 | 6.272
7.85 | 6.28
7.86 | 6.288
7.87 | 6.296
7.88 | 6.304
7.89 | 6.312
7.9 | 6.32
7.91 | 6.328
7.92 | 6.336
7.93 | 6.344
7.94 | 6.352
7.95 | 6.36
7.96 | 6.368
7.97 | 6.376
7.98 | 6.384
7.99 | 6.392
8 | 6.4
8.01 | 6.408
8.02 | 6.416
8.03 | 6.424
8.04 | 6.432
8.05 | 6.44
8.06 | 6.448
8.07 | 6.456
8.08 | 6.464
8.09 | 6.472
8.1 | 6.48
8.11 | 6.488
8.12 | 6.496
8.13 | 6.504
8.14 | 6.512
8.15 | 6.52
8.16 | 6.528
8.17 | 6.536
8.18 | 6.544
8.19 | 6.552
8.2 | 6.56
8.21 | 6.568
8.22 | 6.576
8.23 | 6.584
8.24 | 6.592
8.25 | 6.6
8.26 | 6.608
8.27 | 6.616
8.28 | 6.624
8.29 | 6.632
8.3 | 6.64
8.31 | 6.648
8.32 | 6.656
8.33 | 6.664
8.34 | 6.672
8.35 | 6.68
8.36 | 6.688
8.37 | 6.696
8.38 | 6.704
8.39 | 6.712
8.4 | 6.72
8.41 | 6.728
8.42 | 6.736
8.43 | 6.744
8.44 | 6.752
8.45 | 6.76
8.46 | 6.768
8.47 | 6.776
8.48 | 6.784
8.49 | 6.792
8.5 | 6.8
8.51 | 6.808
8.52 | 6.816
8.53 | 6.824
8.54 | 6.832
8.55 | 6.84
8.56 | 6.848
8.57 | 6.856
8.58 | 6.864
8.59 | 6.872
8.6 | 6.88
8.61 | 6.888
8.62 | 6.896
8.63 | 6.904
8.64 | 6.912
8.65 | 6.92
8.66 | 6.928
8.67 | 6.936
8.68 | 6.944
8.69 | 6.952
8.7 | 6.96
8.71 | 6.968
8.72 | 6.976
8.73 | 6.984
8.74 | 6.992
8.75 | 7
8.76 | 7.008
8.77 | 7.016
8.78 | 7.024
8.79 | 7.032
8.8 | 7.04
8.81 | 7.048
8.82 | 7.056
8.83 | 7.064
8.84 | 7.072
8.85 | 7.08
8.86 | 7.088
8.87 | 7.096
8.88 | 7.104
8.89 | 7.112
8.9 | 7.12
8.91 | 7.128
8.92 | 7.136
8.93 | 7.144
8.94 | 7.152
8.95 | 7.16
8.96 | 7.168
8.97 | 7.176
8.98 | 7.184
8.99 | 7.192
9 | 7.2
9.01 | 7.208
9.02 | 7.216
9.03 | 7.224
9.04 | 7.232
9.05 | 7.24
9.06 | 7.248
9.07 | 7.256
9.08 | 7.264
9.09 | 7.272
9.1 | 7.28
9.11 | 7.288
9.12 | 7.296
9.13 | 7.304
9.14 | 7.312
9.15 | 7.32
9.16 | 7.328
9.17 | 7.336
9.18 | 7.344
9.19 | 7.352
9.2 | 7.36
9.21 | 7.368
9.22 | 7.376
9.23 | 7.384
9.24 | 7.392
9.25 | 7.4
9.26 | 7.408
9.27 | 7.416
9.28 | 7.424
9.29 | 7.432
9.3 | 7.44
9.31 | 7.448
9.32 | 7.456
9.33 | 7.464
9.34 | 7.472
9.35 | 7.48
9.36 | 7.488
9.37 | 7.496
9.38 | 7.504
9.39 | 7.512
9.4 | 7.52
9.41 | 7.528
9.42 | 7.536
9.43 | 7.544
9.44 | 7.552
9.45 | 7.56
9.46 | 7.568
9.47 | 7.576
9.48 | 7.584
9.49 | 7.592
9.5 | 7.6
9.51 | 7.608
9.52 | 7.616
9.53 | 7.624
9.54 | 7.632
9.55 | 7.64
9.56 | 7.648
9.57 | 7.656
9.58 | 7.664
9.59 | 7.672
9.6 | 7.68
9.61 | 7.688
9.62 | 7.696
9.63 | 7.704
9.64 | 7.712
9.65 | 7.72
9.66 | 7.728
9.67 | 7.736
9.68 | 7.744
9.69 | 7.752
9.7 | 7.76
9.71 | 7.768
9.72 | 7.776
9.73 | 7.784
9.74 | 7.792
9.75 | 7.8
9.76 | 7.808
9.77 | 7.816
9.78 | 7.824
9.79 | 7.832
9.8 | 7.84
9.81 | 7.848
9.82 | 7.856
9.83 | 7.864
9.84 | 7.872
9.85 | 7.88
9.86 | 7.888
9.87 | 7.896
9.88 | 7.904
9.89 | 7.912
9.9 | 7.92
9.91 | 7.928
9.92 | 7.936
9.93 | 7.944
9.94 | 7.952
9.95 | 7.96
9.96 | 7.968
9.97 | 7.976
9.98 | 7.984
9.99 | 7.992
10 | 8